## FSM Type
FSM Site
|  | ZON Analog | Analog index | [5 empty] | ZON Digital | Byte | Bit
Room Temperature |  | 1 | 0 | [5 empty] | 1 | 0 | 0
Tower light | (Current ring) | 2 | 1 |  |  | Generator Status | DIG2 | P51 | 2 | 0 | 1
Door sensor | (digital connected to analog) | 3 | 2 |  |  | Mobile Status | DIG3 | P50 | 3 | 0 | 2
|  | 4 | 3 |  |  | Grid Status | Grid Available |  | 4 | 0 | 3 | Copied from dig53
Fuel |  | 5 | 4 |  |  | Smoke detector | Ignition Input | P45 | 5 | 0 | 4
Tower light | Real bulbs count (analog3) | 6 | 5 | [5 empty] | 6 | 0 | 5
Fuel - Raw |  | 7 | 6 |  |  | Fuel sensor |  |  | 7 | 0 | 6
Mains Meter | kWh | 8 | 7 |  |  | On Status | Green/Yellow |  | 8 | 0 | 7 | acording to unit configuration - ignition input, digital2 input or RPM
| A L1 | 9 | 8 | DC A |  |  | Analog1 Digital | P49 | 9 | 1 | 0
| A L2 | 10 | 9 | DC V |  |  | Analog2 Digital | P48 | 10 | 1 | 1
| A L3 | 11 | 10 |  |  | Door Sensor | Analog3 Digital | P47 | 11 | 1 | 2
| V L1-N | 12 | 11 | [5 empty] | 12 | 1 | 3
| V L2-N | 13 | 12 | [5 empty] | 13 | 1 | 4
| V L3-N | 14 | 13 | [5 empty] | 14 | 1 | 5
Tenant Meter1 | kWh | 15 | 14 | [5 empty] | 15 | 1 | 6
| A L1 | 16 | 15 | DC A |  |  |  |  | 16 | 1 | 7
| A L2 | 17 | 16 | DC V |  | Meter Utility |  |  | 17 | 2 | 0
| A L3 | 18 | 17 |  |  | Tenant 1 |  |  | 18 | 2 | 1
Tenant Meter2 | kWh | 19 | 18 |  |  | Tenant 2 |  |  | 19 | 2 | 2
| A L1 | 20 | 19 | DC A |  | Tenant 3 |  |  | 20 | 2 | 3
| A L2 | 21 | 20 | DC V |  | Tenant 4 |  |  | 21 | 2 | 4
| A L3 | 22 | 21 |  |  | Rectifier |  |  | 22 | 2 | 5
Tenant Meter3 | kWh | 23 | 22 |  |  | ex6 (ID1) |  |  | 23 | 2 | 6
| A L1 | 24 | 23 | DC A |  | Generator Controller |  |  | 24 | 2 | 7
| A L2 | 25 | 24 | DC V |  |  | ex6i (ID1) input 1 digital |  | 25 | 3 | 0 | voltage above 5v at ex6i input
| A L3 | 26 | 25 |  |  |  | ex6i (ID1) input 2 digital |  | 26 | 3 | 1 | voltage above 5v at ex6i input
Tenant Meter4 | kWh | 27 | 26 |  |  |  | ex6i (ID1) input 3 digital |  | 27 | 3 | 2 | voltage above 5v at ex6i input
| A L1 | 28 | 27 | DC A |  | A/C 1 On | ex6i (ID1) input 4 digital |  | 28 | 3 | 3 | voltage above 5v at ex6i input
| A L2 | 29 | 28 | DC V |  | A/C 2 On | ex6i (ID1) input 5 digital |  | 29 | 3 | 4 | voltage above 5v at ex6i input
| A L3 | 30 | 29 |  |  | A/C 3 On | ex6i (ID1) input 6 digital |  | 30 | 3 | 5 | voltage above 5v at ex6i input
EX6I ID=1/ Serial | Input 1 | 31 | 30 | EX6SerialTemperature 1 |  |  |  |  | 31 | 3 | 6
| Input 2 | 32 | 31 | EX6SerialTemperature 2 |  | Tenant 5 |  |  | 32 | 3 | 7
| Input 3 | 33 | 32 | EX6SerialTemperature 3 |  | Rectifier Alerts | Critical Alarm |  | 33 | 4 | 0
| Input 4 | 34 | 33 | EX6SerialTemperature 4 |  |  | Urgent Alarm |  | 34 | 4 | 1
| Input 5 | 35 | 34 | EX6SerialTemperature 5 |  |  | Non Urgent Alarm |  | 35 | 4 | 2
| Input 6 | 36 | 35 | EX6SerialTemperature 6 |  |  | Mains Failure |  | 36 | 4 | 3
Generator | Battery level | 37 | 36 | [V] |  |  | Ua Low |  | 37 | 4 | 4
| RPM | 38 | 37 |  |  |  | Ua High |  | 38 | 4 | 5
| Gen. Freq. | 39 | 38 | Hz |  |  | HW Failure |  | 39 | 4 | 6
| V1 | 40 | 39 | V |  |  | Overload |  | 40 | 4 | 7
| V2 | 41 | 40 | V |  | Rectifier Alerts | Us Low |  | 41 | 5 | 0
| V3 | 42 | 41 | V |  |  | Us High |  | 42 | 5 | 1
| I1 | 43 | 42 | A |  |  | Non Urg PFA |  | 43 | 5 | 2
| I2 | 44 | 43 | A |  |  | Urgent PFA |  | 44 | 5 | 3
| I3 | 45 | 44 | A |  |  | RM Redundancy Lost |  | 45 | 5 | 4
| Coolant Temp. | 46 | 45 | C |  |  |  |  | 46 | 5 | 5
| Oil Pressure | 47 | 46 | C |  |  |  |  | 47 | 5 | 6
| Oil Temp. | 48 | 47 | C |  |  |  |  | 48 | 5 | 7
| Grid V1 | 49 | 48 | V |  | Globals | GLOBAL ALARM |  | 49 | 6 | 0 | used for icon color on the tree
| Grid V2 | 50 | 49 | V |  |  | DSE Grid Phase1 available |  | 50 | 6 | 1 | DSE grid phase voltage above 60
| Grid V3 | 51 | 50 | V |  |  | DSE Grid Phase2 available |  | 51 | 6 | 2 | DSE grid phase voltage above 60
|  | 52 | 51 |  |  |  | DSE Grid Phase3 available |  | 52 | 6 | 3 | DSE grid phase voltage above 60
Rectifier | Load 1 Total KWH | 53 | 52 | kWh |  |  | Grid Available |  | 53 | 6 | 4 | If DSE connected - at least one grid phase above 60 OR (Generator off And at least one utility meter phase above 60). If no DSE - (Utility meter connected) AND (Generator relay (dig2) off) AND (Mobile generator (dig3) off)
| U System | 54 | 53 | V |  |  | Generator On |  | 54 | 6 | 5 | copy from DIG8 (On Status) | old logic - not in use - if DSE connected - RPM above 100. if no DSE - Generator relay (dig2) on
| I BAT | 55 | 54 | A |  |  |  |  | 55 | 6 | 6
| I LOAD | 56 | 55 | A |  |  |  |  | 56 | 6 | 7
| Charge state | 57 | 56 | % |  | EX6I ID=2 | ex6i input 1 digital |  | 57 | 7 | 0 | voltage above 5v at ex6i input
Tenant Meter5 | kWh | 58 | 57 |  |  |  | ex6i input 2 digital |  | 58 | 7 | 1 | voltage above 5v at ex6i input
| A L1 | 59 | 58 | DC A |  |  | ex6i input 3 digital |  | 59 | 7 | 2 | voltage above 5v at ex6i input
| A L2 | 60 | 59 | DC V |  |  | ex6i input 4 digital |  | 60 | 7 | 3 | voltage above 5v at ex6i input
| A L3 | 61 | 60 |  |  |  | ex6i input 5 digital |  | 61 | 7 | 4 | voltage above 5v at ex6i input
[7 empty] | ex6i input 6 digital |  | 62 | 7 | 5 | voltage above 5v at ex6i input
[9 empty] | 63 | 7 | 6
[7 empty] | Device connected |  | 64 | 7 | 7
[6 empty] | EX6I ID=3 | ex6i input 1 digital |  | 65 | 8 | 0 | voltage above 5v at ex6i input
[7 empty] | ex6i input 2 digital |  | 66 | 8 | 1 | voltage above 5v at ex6i input
Extra information |  |  |  | dse | comap |  | ex6i input 3 digital |  | 67 | 8 | 2 | voltage above 5v at ex6i input
| Generator controller mode: | Unit.Alarm |  | 0=stop | 0=off |  | ex6i input 4 digital |  | 68 | 8 | 3 | voltage above 5v at ex6i input
|  |  |  | 1=auto | 1=manual |  | ex6i input 5 digital |  | 69 | 8 | 4 | voltage above 5v at ex6i input
|  |  |  | 2=manual | 2-auto |  | ex6i input 6 digital |  | 70 | 8 | 5 | voltage above 5v at ex6i input
[9 empty] | 71 | 8 | 6
[7 empty] | Device connected |  | 72 | 8 | 7
[6 empty] | EX6I ID=4 | ex6i input 1 digital |  | 73 | 9 | 0 | voltage above 5v at ex6i input
[7 empty] | ex6i input 2 digital |  | 74 | 9 | 1 | voltage above 5v at ex6i input
[7 empty] | ex6i input 3 digital |  | 75 | 9 | 2 | voltage above 5v at ex6i input
[7 empty] | ex6i input 4 digital |  | 76 | 9 | 3 | voltage above 5v at ex6i input
[7 empty] | ex6i input 5 digital |  | 77 | 9 | 4 | voltage above 5v at ex6i input
[7 empty] | ex6i input 6 digital |  | 78 | 9 | 5 | voltage above 5v at ex6i input
[9 empty] | 79 | 9 | 6
[7 empty] | Device connected |  | 80 | 9 | 7
Note on N56: Itamar: If DSE connected - at least one grid phase above 60 OR (Generator off And at least one utility meter phase above 60) THE "If DSE connected - at least one grid phase above 60 OR (Generator off And at least one utility meter phase above 60)" section is at the case where the DSE was not wired to grid.. we have a situation where the generator is off, no grid information, but we have 220v at the utility.. the 220v must come form somwhere...

## FMS Type
FMS Site
|  | ZON Analog | Analog index |  |  | ZON Digital | Byte | Bit
|  | 1 | 0 |  |  | 1 | 0 | 0
|  | 2 | 1 |  |  | 2 | 0 | 1
|  | 3 | 2 |  |  | 3 | 0 | 2
Direct connection to Generator battery |  | 4 | 3 |  |  | 4 | 0 | 3
Fuel |  | 5 | 4 |  |  | 5 | 0 | 4
|  | 6 | 5 | DSE connected |  | 6 | 0 | 5
Fuel - Raw |  | 7 | 6 | Fuel sensor |  | 7 | 0 | 6
|  | 8 | 7 | On Status | Green/Yellow | 8 | 0 | 7 | acording to unit configuration - ignition input, digital2 input or RPM
|  | 9 | 8 |  |  | 9 | 1 | 0
|  | 10 | 9 |  |  | 10 | 1 | 1
|  | 11 | 10 |  |  | 11 | 1 | 2
|  | 12 | 11 |  |  | 12 | 1 | 3
|  | 13 | 12 |  |  | 13 | 1 | 4
|  | 14 | 13 |  |  | 14 | 1 | 5
|  | 15 | 14 |  |  | 15 | 1 | 6
|  | 16 | 15 |  |  | 16 | 1 | 7
|  | 17 | 16 |  |  | 17 | 2 | 0
|  | 18 | 17 |  |  | 18 | 2 | 1
|  | 19 | 18 |  |  | 19 | 2 | 2
|  | 20 | 19 |  |  | 20 | 2 | 3
|  | 21 | 20 |  |  | 21 | 2 | 4
|  | 22 | 21 |  |  | 22 | 2 | 5
|  | 23 | 22 |  |  | 23 | 2 | 6
|  | 24 | 23 | Generator Controller |  | 24 | 2 | 7 | copied from digital6 - for competability with FSM
|  | 25 | 24 |  |  | 25 | 3 | 0
|  | 26 | 25 |  |  | 26 | 3 | 1
|  | 27 | 26 |  |  | 27 | 3 | 2
|  | 28 | 27 |  |  | 28 | 3 | 3
|  | 29 | 28 |  |  | 29 | 3 | 4
|  | 30 | 29 |  |  | 30 | 3 | 5
|  | 31 | 30 |  |  | 31 | 3 | 6
|  | 32 | 31 |  |  | 32 | 3 | 7
|  | 33 | 32 |  |  | 33 | 4 | 0
|  | 34 | 33 |  |  | 34 | 4 | 1
|  | 35 | 34 |  |  | 35 | 4 | 2
|  | 36 | 35 |  |  | 36 | 4 | 3
Generator | Battery level | 37 | 36 |  |  | 37 | 4 | 4
| RPM | 38 | 37 |  |  | 38 | 4 | 5
|  | 39 | 38 |  |  | 39 | 4 | 6
|  | 40 | 39 |  |  | 40 | 4 | 7
|  | 41 | 40 |  |  | 41 | 5 | 0
|  | 42 | 41 |  |  | 42 | 5 | 1
|  | 43 | 42 |  |  | 43 | 5 | 2
|  | 44 | 43 |  |  | 44 | 5 | 3
|  | 45 | 44 |  |  | 45 | 5 | 4
|  | 46 | 45 |  |  | 46 | 5 | 5
|  | 47 | 46 |  |  | 47 | 5 | 6
|  | 48 | 47 |  |  | 48 | 5 | 7
|  | 49 | 48 | Globals |  | 49 | 6 | 0
|  | 50 | 49 |  |  | 50 | 6 | 1
|  | 51 | 50 |  |  | 51 | 6 | 2
|  | 52 | 51 |  |  | 52 | 6 | 3
|  | 53 | 52 |  |  | 53 | 6 | 4
|  | 54 | 53 |  | Generator On | 54 | 6 | 5 | copy from DIG8 (On Status)
|  | 55 | 54 |  |  | 55 | 6 | 6
|  | 56 | 55 |  |  | 56 | 6 | 7
|  | 57 | 56

## Power sources
OFF GRID |  |  | ON GRID
| source |  |  |  | source
GENERATOR | grid | none | grid |  | Generator | (DSE connected & RPM>0) OR (No DSE and Relay digital 2 On)
| generator | (DSE connected & RPM>0) OR (No DSE and Relay digital 2 On) |  |  | Grid | (DSE connected & at least one phase detected) OR (no DSE and Relay digital2 Off)
| rectifier | unit has power | ATS | GENERATOR | Rectifier | unit has power
UTILITY METR
UTILITY METR
RECTIFIER
RECTIFIER
TENANT 1
TENANT 2
… |  |  | TENANT 1
TENANT x |  |  | TENANT 2
…
TENANT x

## Definitions
Generator-Status | Taken from Digital8, and configured in unit (Ignition switch, Digital2, RPM)
Engine Hours | If reported from DSE - taken from the DSE as-is. If no DSE engine hours information - accumulated according to the Generator-Status

## Analog Setting
ZON Analog | Alarm Name | Name | Analog index
1 | Room Temperature |  | 0
2 | Tower light | (Current ring) | 1
3 | Door sensor | (digital connected to analog) | 2
4 |  |  | 3
5 | Fuel |  | 4
6 | Tower light | Real bulbs count (analog3) | 5
7 | Fuel - Raw |  | 6
8 | Mains Meter | kWh | 7
9 |  | A L1 | 8 | DC A
10 |  | A L2 | 9 | DC V
11 |  | A L3 | 10
12 |  | V L1-N | 11
13 |  | V L2-N | 12
14 |  | V L3-N | 13
15 | Tenant Meter1 | kWh | 14
16 |  | A L1 | 15 | DC A
17 |  | A L2 | 16 | DC V
18 |  | A L3 | 17
19 | Tenant Meter2 | kWh | 18
20 |  | A L1 | 19 | DC A
21 |  | A L2 | 20 | DC V
22 |  | A L3 | 21
23 | Tenant Meter3 | kWh | 22
24 |  | A L1 | 23 | DC A
25 |  | A L2 | 24 | DC V
26 |  | A L3 | 25
27 | Tenant Meter4 | kWh | 26
28 |  | A L1 | 27 | DC A
29 |  | A L2 | 28 | DC V
30 |  | A L3 | 29
31 | EX6I ID=1/ Serial | Input 1 | 30 | EX6SerialTemperature 1
32 |  | Input 2 | 31 | EX6SerialTemperature 2
33 |  | Input 3 | 32 | EX6SerialTemperature 3
34 |  | Input 4 | 33 | EX6SerialTemperature 4
35 |  | Input 5 | 34 | EX6SerialTemperature 5
36 |  | Input 6 | 35 | EX6SerialTemperature 6
37 | Generator | Battery level | 36 | [V]
38 |  | RPM | 37
39 |  | Gen. Freq. | 38 | Hz
40 |  | V1 | 39 | V
41 |  | V2 | 40 | V
42 |  | V3 | 41 | V
43 |  | I1 | 42 | A
44 |  | I2 | 43 | A
45 |  | I3 | 44 | A
46 |  | Coolant Temp. | 45 | C
47 |  | Oil Pressure | 46 | C
48 |  | Oil Temp. | 47 | C
49 |  | Grid V1 | 48 | V
50 |  | Grid V2 | 49 | V
51 |  | Grid V3 | 50 | V
52 |  |  | 51
53 | Rectifier | Load 1 Total KWH | 52 | kWh
54 |  | U System | 53 | V
55 |  | I BAT | 54 | A
56 |  | I LOAD | 55 | A
57 |  | Charge state | 56 | %
58 | Tenant Meter5 | kWh | 57
59 |  | A L1 | 58 | DC A
60 |  | A L2 | 59 | DC V
61 |  | A L3 | 60
| Extra information |  |  | dse | comap
Unit.Alarm |  | Generator controller mode: |  | 0=stop | 0=off
|  |  |  | 1=auto | 1=manual
|  |  |  | 2=manual | 2-auto

## Digital Settings
ZON Digital |  |  |  | Byte | Bit
1 |  |  |  | 0 | 0
2 | Generator Status | DIG2 | P51 | 0 | 1
3 | Mobile Status | DIG3 | P50 | 0 | 2
4 | Grid Status | Grid Available |  | 0 | 3 | Copied from dig53
5 | Smoke detector | Ignition Input | P45 | 0 | 4
6 |  |  |  | 0 | 5
7 | Fuel sensor |  |  | 0 | 6
8 | On Status | Green/Yellow |  | 0 | 7 | acording to unit configuration - ignition input, digital2 input or RPM
9 |  | Analog1 Digital | P49 | 1 | 0
10 |  | Analog2 Digital | P48 | 1 | 1
11 | Door Sensor | Analog3 Digital | P47 | 1 | 2
12 |  |  |  | 1 | 3
13 |  |  |  | 1 | 4
14 |  |  |  | 1 | 5
15 |  |  |  | 1 | 6
16 |  |  |  | 1 | 7
17 | Meter Utility |  |  | 2 | 0
18 | Tenant 1 |  |  | 2 | 1
19 | Tenant 2 |  |  | 2 | 2
20 | Tenant 3 |  |  | 2 | 3
21 | Tenant 4 |  |  | 2 | 4
22 | Rectifier |  |  | 2 | 5
23 | ex6 (ID1) |  |  | 2 | 6
24 | Generator Controller |  |  | 2 | 7
25 |  | ex6i (ID1) input 1 digital |  | 3 | 0 | voltage above 5v at ex6i input
26 |  | ex6i (ID1) input 2 digital |  | 3 | 1 | voltage above 5v at ex6i input
27 |  | ex6i (ID1) input 3 digital |  | 3 | 2 | voltage above 5v at ex6i input
28 | A/C 1 On | ex6i (ID1) input 4 digital |  | 3 | 3 | voltage above 5v at ex6i input
29 | A/C 2 On | ex6i (ID1) input 5 digital |  | 3 | 4 | voltage above 5v at ex6i input
30 | A/C 3 On | ex6i (ID1) input 6 digital |  | 3 | 5 | voltage above 5v at ex6i input
31 |  |  |  | 3 | 6
32 | Tenant 5 |  |  | 3 | 7
33 | Rectifier Alerts | Critical Alarm |  | 4 | 0
34 |  | Urgent Alarm |  | 4 | 1
35 |  | Non Urgent Alarm |  | 4 | 2
36 |  | Mains Failure |  | 4 | 3
37 |  | Ua Low |  | 4 | 4
38 |  | Ua High |  | 4 | 5
39 |  | HW Failure |  | 4 | 6
40 |  | Overload |  | 4 | 7
41 | Rectifier Alerts | Us Low |  | 5 | 0
42 |  | Us High |  | 5 | 1
43 |  | Non Urg PFA |  | 5 | 2
44 |  | Urgent PFA |  | 5 | 3
45 |  | RM Redundancy Lost |  | 5 | 4
46 |  |  |  | 5 | 5
47 |  |  |  | 5 | 6
48 |  |  |  | 5 | 7
49 | Globals | GLOBAL ALARM |  | 6 | 0 | used for icon color on the tree
50 |  | DSE Grid Phase1 available |  | 6 | 1 | DSE grid phase voltage above 60
51 |  | DSE Grid Phase2 available |  | 6 | 2 | DSE grid phase voltage above 60
52 |  | DSE Grid Phase3 available |  | 6 | 3 | DSE grid phase voltage above 60
53 |  | Grid Available |  | 6 | 4 | If DSE connected - at least one grid phase above 60 OR (Generator off And at least one utility meter phase above 60). If no DSE - (Utility meter connected) AND (Generator relay (dig2) off) AND (Mobile generator (dig3) off)
54 |  | Generator On |  | 6 | 5 | copy from DIG8 (On Status)
55 |  |  |  | 6 | 6
56 |  |  |  | 6 | 7
57 | EX6I ID=2 | ex6i input 1 digital |  | 7 | 0 | voltage above 5v at ex6i input
58 |  | ex6i input 2 digital |  | 7 | 1 | voltage above 5v at ex6i input
59 |  | ex6i input 3 digital |  | 7 | 2 | voltage above 5v at ex6i input
60 |  | ex6i input 4 digital |  | 7 | 3 | voltage above 5v at ex6i input
61 |  | ex6i input 5 digital |  | 7 | 4 | voltage above 5v at ex6i input
62 |  | ex6i input 6 digital |  | 7 | 5 | voltage above 5v at ex6i input
63 |  |  |  | 7 | 6
64 |  | Device connected |  | 7 | 7
65 | EX6I ID=3 | ex6i input 1 digital |  | 8 | 0 | voltage above 5v at ex6i input
66 |  | ex6i input 2 digital |  | 8 | 1 | voltage above 5v at ex6i input
67 |  | ex6i input 3 digital |  | 8 | 2 | voltage above 5v at ex6i input
68 |  | ex6i input 4 digital |  | 8 | 3 | voltage above 5v at ex6i input
69 |  | ex6i input 5 digital |  | 8 | 4 | voltage above 5v at ex6i input
70 |  | ex6i input 6 digital |  | 8 | 5 | voltage above 5v at ex6i input
71 |  |  |  | 8 | 6
72 |  | Device connected |  | 8 | 7
73 | EX6I ID=4 | ex6i input 1 digital |  | 9 | 0 | voltage above 5v at ex6i input
74 |  | ex6i input 2 digital |  | 9 | 1 | voltage above 5v at ex6i input
75 |  | ex6i input 3 digital |  | 9 | 2 | voltage above 5v at ex6i input
76 |  | ex6i input 4 digital |  | 9 | 3 | voltage above 5v at ex6i input
77 |  | ex6i input 5 digital |  | 9 | 4 | voltage above 5v at ex6i input
78 |  | ex6i input 6 digital |  | 9 | 5 | voltage above 5v at ex6i input
79 |  |  |  | 9 | 6
80 |  | Device connected |  | 9 | 7
Note on G54: Itamar: If DSE connected - at least one grid phase above 60 OR (Generator off And at least one utility meter phase above 60) THE "If DSE connected - at least one grid phase above 60 OR (Generator off And at least one utility meter phase above 60)" section is at the case where the DSE was not wired to grid.. we have a situation where the generator is off, no grid information, but we have 220v at the utility.. the 220v must come form somwhere...